## Study Matrix
Seq # | Project Phase | Study Name | Scope | Performed By | Typical Software | Key Inputs | Key Outputs
1 | 1. Feasibility / Screening | Feasibility Study | Utility | Utility / ISO planning engineer | TARA (power flow screening); ASPEN (short circuit screening) | Interconnection/large-load request (MW, Utility Tie location, BTM IPP nameplate data); existing system base case | Preliminary feasibility flag; rough order-of-magnitude upgrade cost/timeline
2 | 2. System Impact Study (SIS) | Thermal (Loading) Study | Utility | Utility / ISO planning engineer | TARA | System base case + request added; N-1/N-1-1 contingency list; equipment normal & emergency ratings | Thermally overloaded lines/transformers/cables under normal & contingency conditions; required upgrades
3 | 2. System Impact Study (SIS) | Load Flow & Reactive Power Study | Utility | Utility / ISO planning engineer | TARA | Base case; generation/load dispatch scenarios; BTM IPP export profile | Voltage profile; MW/Mvar flows; required reactive power range/power factor at the Utility Tie
4 | 2. System Impact Study (SIS) | Short Circuit & Effective Grounding Study | Utility | Utility / ISO protection engineer - runs the utility's own confidential grid model | ASPEN | Utility grid model (utility-only, not shared with EOR); EOR-submitted equipment data only - BTM IPP/GSU transformer impedance, fault contribution parameters per standard interconnection application forms (data, not a study) | Max/min fault duty at the Utility Tie & neighboring buses; effective grounding (X0/X1, R0/X1) confirmation
5 | 2. System Impact Study (SIS) | TOV (Temporary Overvoltage) Study | Utility | Utility / ISO planning engineer (occasionally an EOR-retained consultant) | PSLF/PSS/E (dynamic simulation); ASPEN (fault-driven overvoltage calc) | Grounding configuration; load-rejection & ground-fault scenarios; BTM IPP characteristics | Max TOV magnitude & duration at the Utility Tie and substation buses
6 | 2. System Impact Study (SIS) | Dynamic Stability Study (System-Wide) | Utility | Utility / ISO planning engineer, using an EOR+OEM-supplied RMS dynamic model | PSLF/PSS/E | EOR+OEM plant dynamic model (LVRT/HVRT curves, controls) in RMS format; system-wide stability base case | Stability/ride-through compliance requirement the plant must meet
7 | 2. System Impact Study (SIS) | System Impact Assessment Report (SIAR) | Utility | Utility / ISO | Compiles TARA / ASPEN / PSLF-PSS-E outputs | Results of rows 2-6 | Consolidated report identifying all required network upgrades & constraints
8 | 3. Facilities Study / Interconnection Agreement | Facilities Study | Utility | Utility / ISO | TARA | SIAR results; utility design standards/practices | Scope, cost, and schedule for utility-side upgrades
9 | 4. Detailed Design - EOR / EOR+OEM | Harmonic Study (Pre-Construction) | EOR+OEM | EOR power systems engineer with BTM IPP OEM (converter harmonic data) | ETAP/SKM (frequency-domain analysis); PSCAD (converter-level injection profile, from the OEM's EMT model) | Utility frequency-scan impedance data; BTM IPP converter/inverter harmonic current spectra (from OEM) | Predicted voltage/current distortion (THD & individual harmonics) vs. IEEE 519 limits
10 | 4. Detailed Design - EOR / EOR+OEM | Short Circuit & Grounding Study - EOR | EOR | EOR power systems engineer | ETAP/SKM | Fault duty at the Utility Tie per the Utility Short Circuit Study (row 4 - required first); substation one-line & equipment data | Substation/Utility Tie equipment fault-current ratings; grounding grid design
11 | 4. Detailed Design - EOR / EOR+OEM | Switching Transient Study | EOR | EOR power systems engineer | EMTP-RV (or PSCAD when a detailed OEM converter EMT model is needed for the same switching cases) | Breaker/capacitor-bank switching scenarios; line/cable energization cases | Fast transient overvoltage magnitudes (microsecond-millisecond range)
12 | 4. Detailed Design - EOR / EOR+OEM | Insulation Coordination Study | EOR | EOR power systems engineer | EMTP-RV (or PSCAD, same tool choice as row 11) | TOV results (row 5); switching transient results (row 11); adjacent utility equipment BIL | Arrester ratings & placement; BIL selection for substation equipment
13 | 4. Detailed Design - EOR / EOR+OEM | Dynamic Model Validation & Initial Control Settings (EMT) | EOR+OEM | EOR power systems engineer with BTM IPP/BESS/STATCOM OEM | PSCAD | Utility ride-through requirement (row 6); OEM EMT controller model | Calculated initial LVRT/HVRT settings and ramp-rate/smoothing control parameters (preliminary - actual tuning happens in the field, row 22); validated EMT model for utility submission
14 | 4. Detailed Design - EOR / EOR+OEM | Protection Coordination (TCC Curves) - EOR | EOR | EOR protection engineer | ETAP/SKM | Fault current data (row 10); equipment damage curves; utility relay requirements at the Utility Tie | Relay settings; TCC coordination curves for substation & Utility Tie equipment
15 | 4. Detailed Design - EOR / EOR+OEM | Arc Flash Study - EOR | EOR | EOR power systems engineer | ETAP/SKM | Short circuit results (row 10); protective device clearing times | Incident energy; PPE category; arc flash labels for substation & Utility Tie equipment
16 | 4. Detailed Design - EOR / EOR+OEM | Protection Coordination (TCC Curves) - BTM IPP Package | EOR+OEM | BTM IPP OEM package engineer, coordinated with EOR | ETAP/SKM | OEM package fault current & equipment damage curves; EOR substation relay requirements | Relay/coordination settings for the OEM's own generation package switchgear
17 | 4. Detailed Design - EOR / EOR+OEM | Arc Flash Study - BTM IPP Package | EOR+OEM | BTM IPP OEM package engineer, coordinated with EOR | ETAP/SKM | OEM package short circuit results; protective device clearing times | Incident energy; PPE category; arc flash labels for OEM package equipment
18 | 5. Detailed Design - Facility/EPC (Data Center) | Short Circuit & Grounding Study - Facility | Facility/EPC | Data center owner's engineer / EPC | ETAP/SKM | Fault duty at the MV handoff point (from EOR, row 10); data center one-line & equipment list | Data center equipment fault ratings; grounding design
19 | 5. Detailed Design - Facility/EPC (Data Center) | Protection Coordination (TCC Curves) - Facility | Facility/EPC | Data center owner's engineer / EPC | ETAP/SKM | Fault duty (row 18); data center equipment damage curves | Relay/breaker/fuse coordination within the data center
20 | 5. Detailed Design - Facility/EPC (Data Center) | Arc Flash Study - Facility | Facility/EPC | Data center owner's engineer / EPC | ETAP/SKM | Rows 18-19 results | Incident energy; PPE category; arc flash labels for data center MV/LV equipment
21 | 6. Commissioning / Compliance Verification | Harmonic Compliance Test | EOR+OEM | EOR/OEM commissioning engineer; Utility may witness | Field power quality measurement, validated against the ETAP/SKM model | Field harmonic measurements at the Utility Tie / MV handoff point | Confirms as-built compliance with IEEE 519 vs. the pre-construction study (row 9)
22 | 6. Commissioning / Compliance Verification | Ride-Through & Reactive Power Field Tuning and Compliance Test | EOR+OEM | EOR/OEM commissioning engineer; Utility/ISO witnesses | Field test, validated against the PSCAD EMT model | Initial settings from row 13; field disturbance/injection test results | FINAL tuned LVRT/HVRT settings and reactive power control parameters - actual field tuning happens here, not in row 13; confirms as-built compliance with row 6's requirement

## Legend & Definitions
Project Topology & Scope Categories
Chain | Utility grid -> Utility Tie (POI/POD) -> Substation & BTM IPP (EOR / EOR+OEM) -> MV handoff -> Data Center (Facility/EPC)
Utility | The interconnecting utility or ISO. Owns and studies everything on their system up to and including the Utility Tie.
EOR | Engineer of Record for the substation and Utility Tie - the balance-of-plant interconnection design that is not specific to the BTM IPP's own equipment package.
EOR+OEM | Studies specific to the BTM IPP's own generation package - its technology (engines/turbines/fuel cells, BESS, STATCOM) and that package's own switchgear/controls. The OEM performs or supplies the core technical model and package-specific studies (protection, arc flash, harmonics, EMT controls model); the EOR integrates these into the overall interconnection design.
Facility/EPC | The data center owner's own engineer or EPC. Scope: everything from the MV handoff point down into the data center's own electrical system (main MV switchgear, transformers, UPS, PDUs, IT load).
Why the Utility Short Circuit Study Comes Before the EOR's
Sequence | Row 4 (Utility) must complete before row 10 (EOR). The utility runs the short circuit study on its own confidential grid model, which the EOR never has access to. The EOR's only role at that stage is submitting standard equipment data - BTM IPP/GSU transformer impedance, fault contribution parameters - via the interconnection application forms. That is data, not a study. The utility then returns a fault duty value at the Utility Tie, and that number becomes a required input to the EOR's own Short Circuit & Grounding Study (row 10), which sizes EOR-scope equipment and grounding. The EOR study cannot be finalized until the utility publishes that number.
What is the "Thermal Study" inside the System Impact Study?
Definition | The thermal (loading) study checks whether adding the BTM IPP/data center load causes any existing line, transformer, cable, or breaker to exceed its normal or emergency (contingency) rating. It is a power-flow-based analysis - the same base case as the Load Flow & Reactive Power Study (row 3) - but the pass/fail criterion is equipment thermal capacity rather than bus voltage.
Why it matters | Overloads found here are the main driver of the utility's required network upgrades - usually the single biggest driver of interconnection cost and timeline.
Why There's No Standalone "Load Flow Study" on the Facility/EPC Side
Explanation | "Load flow" is a grid-level System Impact Study concept (row 3) - assessing voltage and Mvar flow across a meshed or looped utility network, and setting the reactive power requirement the plant must meet. Inside the data center's own radial MV/LV distribution there is no equivalent network-flow question - the comparable engineering (transformer/cable sizing, voltage drop) is basic electrical design, not a discrete named study. It is folded directly into the Facility short circuit, protection, and arc flash studies (rows 18-20) rather than treated as its own line item.
Initial Settings vs. Field Tuning
Explanation | Row 13 (Dynamic Model Validation & Initial Control Settings) produces calculated, model-based settings - a starting point, not a final answer. Actual tuning of LVRT/HVRT and reactive power controls happens in the field during commissioning (row 22), once the equipment is live and its real performance can be measured against the ride-through requirement the utility set in row 6. Calling row 13 "tuning" overstates what can be done on paper before the plant exists.
TOV vs. Switching Transients vs. Insulation Coordination
TOV Study | Power-frequency overvoltages lasting cycles to seconds (ground faults, load rejection, ferroresonance). Drives arrester MCOV/continuous rating selection.
Switching Transient Study | Fast transients lasting microseconds to milliseconds (breaker operations, capacitor bank switching, line/cable energization), normally run in EMTP-RV; PSCAD substitutes when a detailed OEM converter EMT model is needed for the same switching cases. Drives arrester energy duty and BIL margin.
Insulation Coordination Study | The umbrella deliverable: combines TOV and switching transient results to select BIL levels and specify/place surge arresters. TOV alone is not the same thing as insulation coordination - it is one of two required inputs.
Software Tool Boundaries
TARA | Utility/ISO steady-state power flow, thermal loading, and transfer capability analysis. Grid-wide, Utility scope only.
ASPEN (OneLiner) | Utility/ISO system-wide short circuit, effective grounding, and protective relay database work. Runs on the utility's confidential grid model - not available to the EOR.
PSLF/PSS/E | Utility/ISO RMS-domain (positive-sequence) dynamic and transient stability simulation - the system-wide ride-through/dynamic study and TOV. Fast enough to run across the whole interconnected grid, but cannot resolve sub-cycle converter switching detail. No PSCAD substitute at this system-wide scale.
EMTP-RV | Apparatus-level electromagnetic transient (EMT) analysis for conventional equipment - switching transients and insulation coordination at the substation/Utility Tie. EOR scope. PSCAD is an acceptable substitute whenever a detailed OEM converter model is required for the same case (rows 11-12).
PSCAD | EMT-domain validation of the BTM IPP/BESS/STATCOM's own converter controls - the detailed, OEM-supplied model used to set initial ride-through/control parameters (row 13) and to validate field tuning (row 22). Also usable in place of EMTP-RV for switching transient/insulation coordination cases that need OEM converter detail (rows 11-12), and for the converter-level harmonic injection profile (row 9).
ETAP/SKM | EOR, OEM-package, and Facility/EPC plant-level studies: short circuit, protection coordination (TCC), arc flash, harmonic analysis. Not used for grid-wide utility studies.
Abbreviation Glossary
Utility Tie / POI / POD | Point of Interconnection / Point of Delivery between the utility and the EOR-scope facility
BTM IPP | Behind-The-Meter Independent Power Producer - generation located on the customer side of the Utility Tie
SIS / SIAR | System Impact Study / System Impact Assessment Report
IA | Interconnection Agreement
TOV | Temporary Overvoltage
TCC | Time-Current Curve (protective device coordination)
LVRT / HVRT | Low/High Voltage Ride-Through
BIL | Basic Insulation Level
MCOV | Maximum Continuous Operating Voltage (surge arrester rating)
THD | Total Harmonic Distortion
IEEE 519 | IEEE standard limiting harmonic distortion on the power system
NFPA 70E / OSHA | US workplace electrical safety standard / federal enforcement agency governing arc flash PPE
EMT / RMS | Electromagnetic Transient (PSCAD/EMTP-RV) vs. Root-Mean-Square positive-sequence (PSLF/PSS/E) simulation domains
EOR | Engineer of Record
OEM | Original Equipment Manufacturer - here, the BTM IPP generation/BESS/STATCOM package supplier
STATCOM | Static Synchronous Compensator (reactive power/voltage support device)
BESS | Battery Energy Storage System